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	· Powered with AC 24V or DC 24V

· Temperature and humidity measurement
· Temperature or temperature and humidity control

· Heating and cooling

· DC 0…10V control of heating / cooling actuators
· 6-port ball valve as changeover (On/Off – open/close signal) and combi valve (PICV) DC 0…10 V
· Automatic or manual fan speed control: DC Fan
· Multifunctional inputs for keycard contact, external sensor, etc.

· Adjustable commissioning and control parameters

· Backlit LCD

· KNX bus communications

	
	


	Plant diagram
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	Description 
of general functions 
	When"4-pipe fan coil unit with PICV and 6-port ball valve as changeover" is selected (via DIP switches or tool), the following functions are available.
For details see basic documentation (A6V11545892 for RDG260KN)


	
	Control sequence 
	
	

	
	· Control of combi valve (PICV) in combination with a 6-port ball valve as changeover (On/Off or DC 0…10 V)

	
	· Heating and cooling
	
	

	
	
	
	Other functions

	
	Fan control
	
	· Button lock

	
	· DC fan, automatic
	
	· 2nd line display setting

	
	· Manual speed control on room thermostat
	
	· Setting access with password protection

	
	· Fan control in dead zone
	
	· Valve exercising to prevent from gripping

	
	· Fan start related to the coil temperature
	
	

	
	
	
	Humidity control

	
	Room and humidity temperature measurement
	
	· By shifting temperature setpoint

	
	· Internal sensor
	
	· By controlling an external equipment

	
	· External room temperature sensor
	
	

	
	· External return air sensor
	
	3 multifunctional inputs

	
	
	
	· Temperature (room, return air, changeover …)

	
	
	
	· Digital (changeover, presence, window contact …)

	Device list
	<START StandardDeviceList>
Legend 

Type of unit 

Data sheet 

Product No. 

Qty. 

N1

Room thermostat with KNX communications, AC 24 V or DC 24 V, for fan coil units and universal applications

A6V11545853

RDG260KN

1

YHC

Combi-Valves (PICV)  

N4855

VPI46..

1

Electrical actuator, DC 0...10 V
(for Combi-Valves VPI45)

N4893

SSA61..

1

C/O

6-port control ball valve 

A6V10564480

VWG41…

1 

Motoric actuator for 6-port control ball valve, 3-position

 N4657

GDB331.9E

1  

<END StandardDeviceList>

	
	+ For selection of actuators and valves please refer to the product catalog

	
	


	Optional
	<START OptionalDeviceList>
Legend 

Type of unit 

Data sheet 

Product No. 

Qty. 

B1

Cable temperature sensor PVC 2.5 m, NTC 3 kOhm, with connectors 2.8 x 0.8 mm
N1840

QAH11

1

<END OptionalDeviceList>


	Variants
	<START VariantsDeviceList>
Legend 

Type of unit 

Data sheet 

Product No. 

Qty. 

B1a

Room temperature sensor NTC 3 kOhm

N1747

QAA32

1

<END VariantsDeviceList>


	Connection diagram
	DC 0…10 V fan
	No fan

	
	[image: image4.wmf]
	[image: image5.wmf]


	
	N1
	Room thermostat RDG260KN
	
	B1, B2, B3
	Optional external sensors 

	
	M1
	DC 0…10 V fan
	
	S1, S2, S3
	Optional switches

	
	V1
	6-port ball valve actuator as changeover (On/Off) 
	
	YHC
	PICV control valve (DC 0…10 V) 

	
	
	
	
	CE+, CE-
	KNX bus

	
	Notes

· Type of control output selectable via DIP switches (On/Off, DC 0…10 V).

· Multifunctional input function selectable via parameters P150…P156 (Room temp. / return air temp, H/C changeover, window contact, dewpoint sensor, fault input)

· 3-speed, 1-speed or DC fan selectable via parameter P351


	Setting option
	Device can be set via

	
	- DIP switches and parameters

- Smartphone APP PCT Go for Android™

- Remotely via KNX tools such as Siemens ACS or ETS5
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	DIP switch settings
	Application
	DIP switches
	Remark

	
	Remote configuration (factory setting)
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	Application, outputs and parameters will be downloaded via commissioning tool
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	DIP No.: 1…8
	DIP No.: 1…8
	

	Application
	4-pipe fan coil unit with PICV and 6-port ball valve as changeover
	[image: image10.wmf]
	Set DIP switches 1 and 4

	Control outputs
	· Combi valve (PICV) DC 0…10 V
	[image: image11.wmf]
	

	Fan
	· DC fan
	[image: image12.wmf]
	Set DIP switch 6


	Main settings
	Function
	Parameters
	Remarks

	Control sequence
	Select the control sequence(s) of the controller
	P001 = 4
	4 = Heating and cooling

	
	
	
	

	General parameters
	User operating mode profile
	P002 = 1…3
	1 = Auto – Protection (Factory setting)

2 = Auto – Comfort – Economy – Protection

3 = Auto – Protection Hospitality

	
	User fan mode selection
	P003 = 0...3
	0 = Auto – Manual (Factory setting)

1 = Manual

2 = Auto – Manual – Protection

3 = Auto – Protection

	
	Standard temperature display
	P008 = 0, 1
	0 = Room temperature (Factory setting)

1 = Setpoint

	
	Additional display information
	P009 = 0…5
	0 = --- (No display) (Factory setting)
1 = °C and °F

2 = Outside temperature (via bus)

3 = Time of day (12 h) (via bus)

4 = Time of day (24 h) (via bus)

5 = Humidity

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	Comfort setpoint
	P011 = 5...40 °C
	Factory setting 21 °C

	
	Economy heating setpoint
	P019 = OFF, 5 °C…P020
	Factory setting 15 °C

	
	Economy cooling setpoint
	P020 =OFF,
P019 …40 °C 
	Factory setting 30 °C

	
	
	P256 = 0…10 V
	Factory setting: 10 V


	Multifunctional inputs, digital input
	External / return air temperature
	P150 = 1
	Factory set on X1

	
	No function
	P153 = 0
	Factory set on X2

	
	Window contact
	P155 = 3
	Factory set on U1

	Inputs selection
	0 = --- (no function)
	
	7 = Monitor input (Digital)(DI)

	
	1 = Room temp ext. sensor / return (AI)
	
	8 = Monitor input (Temp) (AI)

	
	2 = H/C changeover (AI/DI)
	
	9 = Supply air sensor (AI)

	
	3 = Window contact [PROT] (DI)
	
	10 = Presence detector / card reader (DI)

	
	4 = Dewpoint sensor (DI)
	
	11 = External temperature limit (AI)

	
	5 = Enable electric heater (DI)
	
	12 = Coil temperature (AI)

	
	6 = Fault input (DI)
	
	13 = Hotel presence detector / card reader (DI)

	Fan setting
	Fan type 1-speed
	P351 = 1
	

	
	Fan type 3-speed
	P351 = 2
	

	
	DC fan
	P351 = 3
	

	Humidity control
	Control strategy
	P450 = 0
	Only temperature control (default)

	
	
	P450 = 1
	Temperature and humidity control

	
	Humidity setpoint high
	P024 = OFF, P026 or 20…90 %
	Factory setting: 50

	
	Humidity setpoint low
	P026 = OFF, 20…90 % or P024
	Factory setting: OFF

	
	Max. shift temp setpoint (Dehumid.)
	P461 = -3...3 K
	Temperature setpoint deviation due to the humidity in the room

	Engineering
	For a complete list of parameters and detailed description of functions see basic documentation:

A6V11545892 for RDG260KN;

For engineering of RDG in conjunction with Synco see CE1P3127 (Communication via the KNX bus for Synco 700, Basic documentation)



	Heating control
	Evaluation
	Definition 
of classes
	Remarks
	

	
	
	RDG260KN
	Non residential
	

	
	
	
	D
	C
	B
	A
	

	
	Emission control

The control system is installed at the emitter or room level, for case 1 one system can control several rooms
	
	
	
	
	
	

	1. 
	0
	No automatic control
	
	
	
	
	
	

	2. 
	1
	Central automatic control
	
	
	
	
	
	

	3. 
	2
	Individual room automatic control by thermostatic valves or electronic controller
	X
	
	
	
	
	

	4. 
	3
	Individual room control with communication between controllers and to BACS
	
	
	
	
	
	

	5. 
	4
	Integrated individual room control including demand control (by occupancy, air quality, etc.) 
	X
	
	
	
	
	29

	6. 
	Control of distribution network hot water temperature (supply or return)

Similar function can be applied to the control of direct electric heating networks
	
	
	
	
	
	7

	7. 
	0
	No automatic control
	
	
	
	
	
	

	8. 
	1
	Outside temperature compensated control
	
	
	
	
	
	

	9. 
	2
	Indoor temperature control
	
	
	
	
	
	

	10. 
	Control of distribution pumps
The controlled pumps can be installed at different levels in the network
	
	
	
	
	
	7

	11. 
	0
	No control
	
	
	
	
	
	

	12. 
	1
	On off control
	
	
	
	
	
	

	13. 
	2
	Variable speed pump control with constant p
	
	
	
	
	
	

	14. 
	3
	Variable speed pump control with proportional p
	
	
	
	
	
	

	15. 
	Intermittent control of emission and/or distribution
One controller can control different rooms/zone having same occupancy patterns
	
	
	
	
	
	7

	16. 
	0
	No automatic control
	
	
	
	
	
	

	17. 
	1
	Automatic control with fixed time program
	
	
	
	
	
	

	18. 
	2
	Automatic control with optimum start/stop
	
	
	
	
	
	

	19. 
	Generator control
	
	
	
	
	
	7

	20. 
	0
	Constant temperature
	
	
	
	
	
	

	21. 
	1
	Variable temperature depending on outdoor temperature
	
	
	
	
	
	

	22. 
	2
	Variable temperature depending on the load
	
	
	
	
	
	

	23. 
	Sequencing of different generators
	
	
	
	
	
	7

	24. 
	0
	Priorities only based on loads
	
	
	
	
	
	

	25. 
	1
	Priorities based on loads and generator capacities
	
	
	
	
	
	

	26. 
	2
	Priorities based on generator efficiency (check other standard)
	
	
	
	
	
	

	
	



	Cooling control
	Evaluation
	Definition 
of classes
	Remarks
	

	
	
	RDG260KN
	Non residential
	

	
	
	
	D
	C
	B
	A
	

	
	Emission control

The control system is installed at the emitter or room level, for case 1 one system can control several rooms
	
	
	
	
	
	

	27. 
	0
	No automatic control
	
	
	
	
	
	

	28. 
	1
	Central automatic control
	
	
	
	
	
	

	29. 
	2
	Individual room automatic control by thermostatic valves or electronic controller
	X
	
	
	
	
	

	30. 
	3
	Individual room control with communication between controllers and to BACS
	
	
	
	
	
	

	31. 
	4
	Integrated individual room control including demand control (by occupancy, air quality, etc.) 
	X
	
	
	
	
	29

	32. 
	Control of distribution network cold water temperature (supply or return)

Similar function can be applied to the control of direct electric heating networks
	
	
	
	
	
	7

	33. 
	0
	No automatic control
	
	
	
	
	
	

	34. 
	1
	Outside temperature compensated control
	
	
	
	
	
	

	35. 
	2
	Indoor temperature control
	
	
	
	
	
	

	36. 
	Control of distribution pumps
The controlled pumps can be installed at different levels in the network
	
	
	
	
	
	7

	37. 
	0
	No control
	
	
	
	
	
	

	38. 
	1
	On off control
	
	
	
	
	
	

	39. 
	2
	Variable speed pump control with constant p
	
	
	
	
	
	

	40. 
	3
	Variable speed pump control with proportional p
	
	
	
	
	
	

	41. 
	Intermittent control of emission and/or distribution
One controller can control different rooms/zone having same occupancy patterns
	
	
	
	
	
	7

	42. 
	0
	No automatic control
	
	
	
	
	
	

	43. 
	1
	Automatic control with fixed time program
	
	
	
	
	
	

	44. 
	2
	Automatic control with optimum start/stop
	
	
	
	
	
	

	45. 
	Interlock between heating and cooling control of emission and/or distribution
	
	
	
	
	
	7

	46. 
	0
	No interlock
	
	
	
	
	
	

	47. 
	1
	Partial interlock (dependant of the HVAC system)
	
	
	
	
	
	

	48. 
	2
	Total interlock
	
	
	
	
	
	

	49. 
	Generator control
	
	
	
	
	
	7

	50. 
	0
	Constant temperature
	
	
	
	
	
	

	51. 
	1
	Variable temperature depending on outdoor temperature
	
	
	
	
	
	

	52. 
	2
	Variable temperature depending on the load
	
	
	
	
	
	

	53. 
	Sequencing of different generators
	
	
	
	
	
	7

	54. 
	0
	Priorities only based on loads
	
	
	
	
	
	

	55. 
	1
	Priorities based on loads and generator capacities
	
	
	
	
	
	

	56. 
	2
	Priorities based on generator efficiency (check other standard)
	
	
	
	
	
	

	
	

	Summary
	Energy efficiency class: 
RDG260KN
A


	Remarks
	No.
	Remark

	
	7
	Only together with Efficiency Class A application

	
	29
	Presence detector required

	
	
	

	
	Home automation / building automation and control system and technical home/building management required satisfying Efficiency Class A

	
	Efficiency Class rating based on EN15232:2007
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