|  | - Heating or/and cooling - LCD backlit display - ON/OFF control of heating and cooling actuators - Automatic or manual 3-speed fan control - Time with delay Off function - Adjustable commissioning and control parameters - Fit into 86x86 conduit boxes |
| --- | --- |

| Variants for room thermostats | - Backlit for LCD | - Universal Inputs X1 & X2 | - 86x86 conduit boxes - e.g. ARG71 | - Round CEE conduit box - e.g. VDE/DIN |
| --- | --- | --- | --- | --- |
| RDF300.02 |  |  |  |  |
| RDF600 |  |  |  |  |
| RDF600T |  |  |  |  |

| Plant diagram |  |
| --- | --- |

| Function diagram (valve actuators ON/OFF) | Example: heating and cooling mode (P01 = 04) |  |
| --- | --- | --- |
|  |  | T; Room temperature. w; Room temperature setpoint. Y; Output signal. YH; Control command “Valve” (heating). SDH; Switching differential “Heating” (P30). SDC; Switching differential “Cooling” (P31). Xdz; Dead zone (P33). YC; Control command “Valve” (cooling). |

| Function diagram (fan) | Fan control in case of 2-position valve control (ON/OFF) |
| --- | --- |

|  | T[°C] | Room temperature | SDH | Switching differential “Heating” (P30) |
| --- | --- | --- | --- | --- |
|  | w | Room temperature setpoint | SDC | Switching differential “Cooling” (P31) |
|  | Q1 | Fan speed 1 | Xdz | Dead zone (P33) |
|  | Q2 | Fan speed 2 | XpHFan | Switching range for fan “Heating” |
|  | Q3 | Fan speed 3 | XpCFan | Switching range for fan “Cooling” |
|  | Y | Control command “Valve” |  |  |
|  | SDH/SDC [K]; 0.5; 1.0; 1.5; 2.0; 2.5; 3.0; 3.5; 4.0; >4.5. XpHFan/XpCFan [K]; 2; 3; 4; 5; 6; 7; 8; 9; 10. |

| Description of functions | For details, please refer to individual data sheet. e.g. A6V10889950. |  |  |
| --- | --- | --- | --- |
|  | Sequence |  | Room operating modes |
|  | - Control of thermal or motorized valve actuators (ON/OFF) |  | - Comfort and Protection (Off) mode |
|  | - Heating and cooling (P01 = 4, factory setting) |  |  |
|  | - Manual heating / cooling changeover (P01 = 2) |  | Room temperature measurement |
|  |  |  | - Internal sensor |
|  | Fan control |  |  |
|  | - Automatic |  | Setpoint adjustment |
|  | - 1...3-speed manual speed control on room thermostat |  | - Locally on room thermostat (via HMI of thermostat) |
|  | - Fan control in dead zone for Comfort mode (P15) |  |  |
|  | Note: More details about advanced fan settings are available in data sheet. |  |  |

| Device list | <START StandardDeviceList> Legend; Type of unit; Data sheet; Product No.; Qty.. N1; Semi flush-mount room thermostat, 4-pipe fan coils; A6V10889950; RDF530; 1. Y1; 2- or 3-port valve; N4842; V...I46; 1. Actuator for small valves, 2-position or 3-position, AC 230 V; A6V10446174; SUA21/3; 1. Y2; 2- or 3-port valve; N4842; V...I46; 1. Actuator for small valves, 2-position or 3-position, AC 230 V; A6V10446174; SUA21/3; 1. <END StandardDeviceList> |
| --- | --- |
|  | For selection of actuators and valves, please refer to the product catalog. |  |
| Connection diagram |  | N1; RDF room thermostat. M1; 3-speed fan. Y1, Y2; On/Off valves: Siemens SUA21/3. T6.3 A; Internal fuse (6.3 A), replaceable. Notes： - Connect only one fan at a time to output Q on the thermostat. - The fuse supports a total maximum loading (fan and valve) of 5 A.. |

| Variants | <START VariantsDeviceList> Legend; Type of unit; Data sheet; Product No.; Qty.. Y1a; Electrometric ON/OFF valve and actuator; N4867; M..I421..; 1. Y1b; Small valve (externally threaded); N4847; V..P47..; 1. ON/OFF actuator, 2P; N4884 N4865; STP.. SFP..; 1. Y1c; 2- or 3-port valve; N4842; V...I46; 1. Actuator for small valves, 2-position or 3-position, AC 230 V; N4863 N4884; SFA21... STA23; 1. Y2a; Electrometric ON/OFF valve and actuator; N4867; M..I421..; 1. Y2b; Small valve (externally threaded); N4847; V..P47..; 1. ON/OFF actuator, 2P; N4884 N4865; STP.. SFP..; 1. Y2c; 2- or 3-port valve; N4842; V...I46; 1. Actuator for small valves, 2-position or 3-position, AC 230 V; N4863 N4884; SFA21... STA23; 1. <END VariantsDeviceList> |
| --- | --- |

| Parameter settings (fan) | Parameters | Description | Setting range | Factory setting |
| --- | --- | --- | --- | --- |
|  | P15 | Fan control in dead zone for Comfort mode | 0 = Fan off 1 = Fan speed 1 in heating or cooling mode | 1 |
|  | P59 | Fan minimum on-time | 1…6 minutes | 2 minutes |

| Miscellaneous parameters | Parameters | Description | Setting range | Factory setting |
| --- | --- | --- | --- | --- |
|  | P01 | Control sequence | 2 = H/C manual changeover 4 = Heating and cooling | 4 |
|  | P05 | Sensor calibration | -5…+5 K | 0 K |
|  | P06 | Standard temperature display | 0 = Room temperature 1 = Setpoint | 0 |
|  | P09 | Minimum setpoint in Comfort mode | 5 °C | 5 …40 °C |
|  | P10 | Maximum setpoint in Comfort mode | 35 °C | 5 …40 °C |
|  | P14 | Keylock function | 0 | 0 = No lock 1 = Full lock |
|  | P27 | Operating mode settings upon power down | 0 | 0 = Return to previous operating mode or user settings 1 = Protection mode |
|  | P28 | Timer with delay Off | 0 | 0 = Users to set on-time duration 1 to 23 = Preset with a fixed on-time in hours |
|  | P30 | Switching differential in heating mode | 1 K | 0.5…6 K |
|  | P31 | Switching differential in cooling mode | 1 K | 0.5...6 K |
|  | P33 | Deadzone in Comfort mode | 2 K | 0.5...5 K |
|  | P65 | Protection heating setpoint | 8 °C | OFF, 5 °C…Wcoolpro; Wcoolpro=40 °C max. |
|  | P66 | Protection cooling setpoint | OFF | OFF, Wheatpro…40 °C; Wheatpro=5 °C min. |
|  | P71 | Reload factory setting | OFF | OFF = Disable; ON = Reload start ”---“ is displayed for 3 seconds during reload process. |
| Engineering | For a complete list of parameters and detailed description of functions see datasheet A6V10889950. |  |  |  |

Subject  to change.	 2017 Siemens Switzerland Ltd.